
[image: image1.wmf] 

Torrance Fire Department 

Underground Fire Sprinkler Supply & Fire Mains 
Plan Submittal Requirements

If the required information below is not provided on the formal plan submittal plans will not be accepted. Supplemental information or attachments will also not be accepted. Please check boxes to indicate information below has been noted on plans:
· Current editions of NFPA 13 & 24
· Current City of Torrance Business License Required prior to issuance of permit
· Plan submittal requirements and local ordnances can be found at https://www.torranceca.gov/our-city/fire
· Provide a scope describing the project and purpose
· Name of owner and occupant.
· Name, address and contact information of party submitting the plans

· Name, address, license and contact information of contractor 
· Location, including street address

· Point of compass

· Scale
· Size, location and piping arrangement of fire department connections 
· Fire Service Mains:

· Size

· Length

· Location

· Weight

· Materials (All piping and materials shall be listed for fire protection service)
· Provide type and class of piping

· Provide method of corrosion protection (If applicable) 
· Fittings shall be of approved type with joints and pressure class ratings compatible with pipe

· Provide detail of method of joining of pipe and fittings

· Method of restraint

· Refer to City of Torrance Municipal Code for requirements on connection to the municipal water system, cross connections
· Point of connection to city main.

· Sizes, types and locations of valves, valve indicators, regulators, meters, and valve pits.
· Fire Hydrants

· Size and location, including size and number of outlets and whether outlets are equipped with independent gate valves.

· Method of restraint.

· Method of protection from traffic. Provide detail
· Location of city main and nearest fire hydrant 
· Provide note indicating: Fire protection water shall not be engineered or designed to enter into the municipal storm drain or sanitary sewer systems without an appropriate permit.
� EMBED Word.Picture.8  ���








PAGE  
P:\DanTemp\Desktop\Plans\2017 Sprinkler Underground_Plan_Submital_Requirements.doc

[image: image2.wmf] 

_1307432862.doc
[image: image1.png]






