CITY OF TORRANCE FIRE DEPARTMENT

COMMUNITY RISK REDUCTION DEVISION

FIRE DEPARTMENT NOTES – FIRE ALARM INSTALLATIONS – NFPA 72 (2016)

- All fire protection water supply control valves shall be electrically supervised.

- A zone map and legend shall be provided at the Fire Alarm Control Panel (FACP) and annunciator/Remote Operator Control Panel (ROCP). These diagrams shall be durably posted and shall contain the location of all initiating devices or zones, as well as control and power equipment.

- Inside the lockable FACP, provide instructions for silencing and resetting FACP, account numbers and contact information for the monitoring company and responsible party SHALL BE PROVIDED.

- Inside the FACP, a label shall be placed with the location and name of the electrical panel as well as the circuit number that powers the fire alarm system.

- A document panel with most current software shall and plans shall be provided at the main FACP.

- At the electrical panel, a marking with red letters shall be used to label the dedicated breaker for the FACP.  A lock shall also be provided to prevent the circuit from being shut off manually.

- The date of manufacture shall be marked on the batteries and shall be in the “MM/DD/YYYY” format.   A printout from battery manufacturer/distributer is required for verification of date codes.

- Additional Notification may be required.  If a kitchen hood suppression system is installed, it shall be connected/monitored to/by fire alarm system and shall activate notification devices.

- A list of all initiating devices (program) shall be provided on a separate sheet at the time of acceptance test.  This list shall be organized by floor in order to expedite testing.

- At least two representatives from the fire alarm company shall be present at the time of the acceptance test and shall be equipped with all of the necessary testing equipment; such as reliable method of communication-radios/cell phone, canned smoke, heat gun, ladders, etc.

- A 24-hour battery standby test shall be required followed by a 5-minute full alarm test at the end of the 24-hour test period. (When required)

- Keys to reset the FACP, Pull Stations, and any other fire alarm equipment, shall be provided at time of test and placed in a Knox Box.

- A 100% system pre-test shall be performed by installation contractor before scheduling an acceptance test with the fire department.

- NFPA 72 System Record of Completion is required upon final.

- A rough-in (pre wire) inspection MAY BE required on large projects, and final test inspection shall be required and requested at least 48 hours in advance. To schedule an inspection please call the City of Torrance fire Department, Community Risk Reduction Division at (310) 618-2973.

Sole Path Communication:

- Communicators shall be listed with the California State Fire Marshal.

- Cellular alarm communication shall be installed following the requirements of NFPA-72 26.6.3 .3 and installer must follow manufactures recommendations.

- Cellular communications shall be programmed so that the path shall be supervised at intervals not more than 60 minutes.

- Where only one communication path technology is used, any failure of the communication path shall be annunciated at the supervising station within 60 minutes of the failure.

- Installing technician shall indicate the signal strength indicator on each communicator to the Fire Inspector.

- Sole Path communicator will be approved on a case by case basis.